ENCLOSURE-III

DETAIL OF TECHNICAL EQUIPMENTS:

- AIR CONDITIONING SYSTEM:

- A/C PLANT :

- “Carrier” make Screw Chiller with 2 compressors and

capacity of 150 TR water cooled, operating on

F–134 a gas, with microprocessor based control.   			: 2 nos.

- “Westinghouse” make 45 TR capacity package Chiller

consisting of 4 compressors sealed & operating on

F–22 gas.								: 1 no.

- CHILLED WATER PUMP :

a.	25 HP split casing type ‘Beacon’ make coupling set			: 2 nos.

b.	20 HP split casing type ‘Beacon’ make coupling set			: 1 no.

c.	7.5 HP Monobloc type ‘Beacon’ motor pump-set			: 1 no.

- CONDENSOR WATER PUMP :

a.	25 HP split casing type ‘Beacon’ make coupling set			: 2 nos.

b.	20 HP split casing type ‘Beacon’ make coupling set			: 1 no.

c.	7.5 HP Monobloc type ‘Beacon’ make motor pump set		: 1 no.

- COOLING TOWERS :

- ‘Paharpur’ make FRP cooling tower with cross flow

design, PVC fills, gear box, fan & motor, of 185 TR

capacity.								: 1 no.

- ‘Paharpur’ make FRP cooling tower with cross flow

design, PVC fills, gear box, fan & motor, of 90 TR

capacity.								: 2 nos.

- ‘ZECO’ make Air–Handling Units of different capacity

for Embassy Office Building.						: 12 nos.

- Central heating oil fired boilers of “Thermax” make

with primary pump.							: 3 nos.

- Fan Coil Units of 1.0 TR, 1.5 TR, & 2.0 TR as per following:

a.	Ambassador’s Office						: 3 nos.

b.	Ambassador’s Residence					: 9 nos.

c. 	Bulgarian Staff Residence:

- Bigger Apartment: 3rd floor: 3 nos.				: 5 nos. each

- Smaller Apartment: 18 nos.					: 4 nos. each

- M.S. Chilled water & Condenser water piping.

- Window and split-type A/Cs wherever installed

- WATER SUPPLY SYSTEM:

- Underground water tanks to receive the water

from NDMC & Tube-well.						: 2 nos.

- Underground water tank to receive unfiltered

water & to feed to the garden.						: 1 no.

- Underground water tank to receive filtered

water & to provide water to booster pumps.				: 1 no.

- Filtration Pumps :

- 2.0 HP motor pump set to take the water from

unfiltered water tank to send to filtered water tank

through pressurised sand filter (one working & one stand by): 2 nos.

- 5.0 HP Automatic ‘Ejecto’ type pump to lift the water

from filtered water tank & to send to Embassy & residences

through pressure tanks (VFD driven)

(one working & one stand by).				: 3 nos.

- FRP water filtration tanks with filter medias and valves.	: 2 nos.

- Water System:

a. FRP water system with capacity to soften 1000 ltr/hour

with necessary valve etc.						: 2 nos.

- Garden Water pump:

7.5 HP Ejecto pump to pressurize the water lines

for garden.								: 1 no.

- Swimming Pool Pump:

- 5.0 HP pumps to circulate the water of

swimming pool through sand filters				: 2 nos.

(one working & one stand by).

- Fire Pump:

Fire pump of 50 HP capacity to charge the fire

Hydrants in the event of fire.						: 1 no.

- Geysers are installed in apartments & Ambassador

residence for hot water supply.

- Bore-well motor pump set.						: 1 no.

- ELECTRICAL INSTALLATION :

- Electrical Distribution Panels.

- All L.T. panel consisting of A.C.B.’s (M.D.O.) & switch

Fuse units.

3. 	D.G. set of 500 KVA capacity ‘Cummins’ make.			: 1 set

4.	D.G. set of 200 KVA capacity ‘Skoda’ make.			: 1 set

5.	AMF panel for D.G. set.						: 1 no.

6. 	Distribution boxes with MCB’s & Isolators.

7. 	L.T. sub distribution boards at lower & upper basements,

ground, first & second floor.

8.	Capacitor panel with capacitor banks.				: 3 nos.

9.	Garden lights & panel.

10.       Building lighting.

11.       Servo stabilizers.

USER:					CONTRACTOR: