ENCLOSURE I

OPERATION AND MAINTENANCE OF

TECHNICAL INSTALLATION AND EQUIPMENT

The Contractor shall provide the necessary qualified staff to carry out regular servicing and maintenance of the equipment, buildings and land of the User. Service and maintenance will include, but will not be limited to, the following:

# AIR CONDITIONING / HEATING SYSTEMS

# І. Central Air-conditioning plants:

- To operate the central A/C plants consisting of two Carrier make screw chillers of 150 TR. capacity each and one Westinghouse make screw chiller of 45 TR. capacity so as to provide air-conditioning 24 hours a day.

- To record hourly in a log book the following parameters of each central A/C plant when in use (log sheet attached):

- Suction pressure;

- Discharge pressure;

- Phase to phase incoming voltage;

- Compressor motor amperes;

- Condenser pump motor amperes;

- Chiller pump motor amperes;

- Cooling tower(s) motor amperes;

- Water pressure and temperature of inlet and outlet of the condenser and chiller;

- Water level in cooling tower and operation of float valves;

- Dry and wet bulb outside temperature;

- Report on any abnormal performance of any part of the plant and or allied equipment.

- To check daily and to carry out the following jobs:

- Water level in expansion tanks;

- Cleaning of plants;

- Rectification of minor faults;

- Reporting of any other problems;

- Recording and maintaining of required temperature and humidity;

- Cleaning of cooling tower filters;

- Cooling tower water level and noise level;

- Performance of pump;

- Attending to complaints from the Chancery building and from the residential flats;

- Cleaning of swimming pool early morning daily;

- Preparing the tennis court three times a week – Monday, Wednesday & Friday.

- Check-up performed monthly:

To check the electrical panels and its wiring for any loose connections, pitted (fixed and moving) contacts of contactors, to lubricate the moving parts and to undertake corrective actions on the following:

- Cleaning of fans and motors of cooling towers;

- Clean air filters of Air Handling Units;

- Check bearings of pumps, motors and blowers and lubricate as and when   required;

- Changing Cooling Tower water and basin cleaning.

- Cleaning Y Strainers;

- Valve and motor glands water leakage rectifying.

ІІ. Boilers:

- To check and adjust the thermostat to maintain the required temperature inside the buildings;

- To check the firing, oil spray and exhaust smoke and adjust if necessary;

- To stop oil leakage, if any;

- To check oil pressure and water pressure daily;

- To check the functioning of photo switch, pressure switch, thermostat, controller, timer, nozzle, spray and electrode firing and electrode firing and adjust/replace, if defective;

- To operate the softening plants as and when required;

- To check the hardness of water and scale formation in primary coils;

- To check the heat transfer from primary circuit to secondary circuit;

- To check the room temperature corresponding to boiler outlet temperature.

ІІІ. Air Handling Units:

- To keep clean and free of dirt and foreign matters all AHUs and to lubricated regularly all moving parts of the control dampers.

- To examine the V-belts and to adjust the tension to ensure belts are in good condition and properly aligned; when replacement of V-belts of a particular drive is required, to ensure usage of complete set of matching belts;

- To correct excessive vibration by checking all bolts, set screws, foundation bolts and isolators etc.

- To check automatic running of AHU motors through VFD (variable frequency drive);

- The check and clean every 3 months or earlier as required the clogging of coils and dust layer on the surface of coils and fins;

- To inspect monthly all motorized valves and modulating motors to ensure their satisfactory performance with their corresponding thermostat. If the valve is malfunctioning the User is to be informed about the required/recommended replacement of part;

- To inspect and clean the fan housing and blowers annually and to clean all drain pans and drain lines every 3 months.

ІV. Fan Coil Units

To wash with detergent, to oil the motors, to adjust the blowers, to check the motorized valve, to clean the filter, to adjust vibration by tightening nut bolts, to check the electrical connection, to check the motor shaft alignment, to clean the return air filter, to check the grill air temperature and to check if it is corresponding to water temperature in plant room.

В. GENERATING SETS

І. To check daily:

1. Engine oil in sump;

2. Fuel in day tank;

3. Electrolyte level in batteries, to top it up with distilled water, if required (also to check specific gravity of batteries once a month and to record it);

4. Water coolant level in radiator and filling if required;

5. Cleaning the generating sets and panels for keeping them dust and oil free.

ІІ. Diesel Fuel

- To make a request in advance for filling of main diesel storage tank;

- To check the automatic operation of solenoid valves if satisfactory working;

- To fill the day fuel tank of the DG sets as and when required;

- To remove water from day tank, if any;

- To rotate the filter for diesel fuel to settle down the foreign materials;

- To check and rectify the oil leakage if any and to perform line cleaning;

- To clean the oil and air filter.

ІІІ. To record hourly in the Log Book the following characteristics of the Generating Sets during Power Outage:

- Oil pressure and temperature of Engine;

- Water temperature of Engine;

- Battery charging of Engine;

- Phase to Phase voltage generated by the alternator;

- Current drawn Per phase from the alternator;

- Reading of KW;

- Report abnormal working of any part of the GENSET in the Remarks Column;

- Voltage frequency;

- R.P.M. of the set.

## Note: To regularly attend to problems of general nature such as engine not taking load, black smoke, erratic operation of engine, engine starting problem and surging of engine.

## ІV. Generating Control panels, AMF and Power Panel.

To clean the generator control panels every six months and to check for circuit breakers/contactors current transformers, fuse units, protective devices, under voltage coil, cable connections, internal control wiring, all bus bar connections, grounding connections, and working all KWH meters etc.

V. Alternators

1. To check and lubricate the bearings of alternators on the basis of the Hrs run/time periods as per the recommendation of manufacturers;

2.  To check, clean / replace the Carbon brushes as required;

3. To clean and check every 6 months the Control Panel of alternators from dust and loose connections;

4. To attend to voltage drop problems of minor nature such as failure of minor components and their replacement as required;

5. To perform annual mеgger testing of insulation value of the windings of starter and rotor.

С. ELECTRICAL INSTALLATION & EQUIPMENT REPLACEMENT.

- To attend to day to day complaints such as replacement of bulbs, tube, control gear, starters, holders, switches, wires, fitting, MCBs, power switches, relays, contactors, indication lights, elements, timers, fuses, measuring instruments, halogen lamps and swimming pool area lights;

- To check the garden light as and when required;

- To clean the distribution boxes, to tighten the connections and to replace burnt wires;

- To perform preventive servicing of main/sub distribution panels and to replace defective parts annually;

- To check the city mains voltage and to contact the suppliers in case voltage is less than the permissible limits;

- To inform NDMC for oil checking in HT OCBs, transformers, oil test, dehydration of oil and get the job done;

- To inform NDMC for HT tripping, LT tripping and get the supply restored;

- To check the heating of cables and rectify accordingly;

- To check the automatic operation of generators, motor control center, garden light, rain water pumps, boilers and to rectify in case of defect.

### WATER SUPPLY SYSTEM

1.   To start the tube well every day and to close it as per program, to replace and repair the hydrants;

2.   To fill the underground water tank with NDMC / tube well water every day and to clean when required;

3.    To feed the chlorine to drinking water on the basis of requirement;

4.   To back wash the drinking water filtration tank when the water pressure drops down;

5.   To keep all swimming pool re-circulation equipments in working order; to apply chlorine and to clean the swimming pool; to inform the User in advance about requirement of chlorine granules;

6.   To perform preventive maintenance of fire pumps, fire electrical board, fire hydrants to keep the system ready at all times; to test start the fire pump at least once per month;

7.  To check the minor water leakage in the pipe line, such as hot water, drinking water, toilets, garden and rectify accordingly;

8. To maintain 24 Hrs. drinking water supply inside the User compound through automatic operation of the system. To do all necessary preventive maintenance for all water supply equipment to keep them in perfect order and clean. The Contractor will also see that each pump is used on a regularly scheduled rotation basis;

9. To soften the municipal/raw water through the water softeners to fill filtered water underground tank;

10. To record in a Log Book the water meter reading of the 3 main water        supply lines on the first day of every month.

- To attend to day to day complaints for replacements, rectification of W/C, washbasin, kitchen sink, shower, water taps, bath tubs;

- To clean / open the toilets, kitchen pipe lines when these are choked;

- To open the storm water drain/pipe line as and when required;

USER:						CONTRACTOR: